## INPUT DATA
Template for Deign and Estimation of Water Supply System with Surface Water Source | [8 empty] | City | Panipat
Input Dat | [5 empty] | Assumptions | [5 empty] | User Instructions
I | Population
| Year | Population | Households |  |  |  |  | Method/Basis |  |  |  | 1 Where Applicable:This is for augmentation by new surface water source, water pumped from intake
| 1951 | 54981 |  |  |  | I | Population Projections | Available Projected Data | Choose from drop down menu only |  |  | to WTP with sump and RWPS, from WTP water collected in CWR and then by
| 1961 | 67026 | [9 empty] | CWPS pumped directly to different service reservoirs , WTP near the city. Single
| 1971 | 87981 |  |  |  |  | If the above option is "Available Projected Data" enter projected population below |  |  |  |  | stage pumping for raw water and for clear wate. Surface ground generally flat.
| 1981 | 137927 |  |  |  |  | Year | 2011 | 2021 | 2031 | 2041 | 2Input Data:The cells for data input and requiring users review are shaded with different
| 1991 | 191000 |  |  |  |  | Population | 499438 | 701302 | 959740 | 1274752 | colours. Input data or review the data/result according to following color codes:
| 2001 | 261740 | 52000
II | Present Water supply | [5 empty] | If the above option is "Growth Rate based Project" enter below the Decadal Growth Rate to be used for Projection | [5 empty] | Input data to be provided | Enter data if condition
| Year | Population | Quantity | Tube Wells | NRW |  | Decade | Decadal Growth Rate | [5 empty] | satisfies
|  | Nos | MLD | Nos | % |  | Decade | 2001-11 | 2011-21 | 2021-31 | 2031-41 |  | Review the provided values & | No value to be entered
| 2009 | 486000 | 81.05 | 195 | 40 |  | Growth Rate% | [5 empty] | revise/update if required | Calculates automatically
| No of water connections |  |  | 27303 | Nos
| Population Covered |  |  | 137428.6004 | Nos | II | Design Period | [5 empty] | No data to be entered select from drop down menu
| Yearly Revenue Assesment |  | Year 07-08 | 184 | Lac Rs |  | Base Year | Year |  | 2011
| Yearly Revenue Received |  | Year 07-08 | 110.3 | Lac Rs |  | Design Period for Storage/rising main | No. of Years: Choose from drop down | 30 | 2041
| Yearly O & M Expenditure |  | Year 07-08 | 535.13 | Lac Rs | [6 empty] | 3 Output: 6 output tables are given which is final output and shall be part of report
| No of Employees |  |  | 283 | Nos | III | Market Rates |  | Rs | DI K7 Dia in mm | Rs/meter | 4 Population Projection: This tool gives population projection by different
| Road Length |  |  | 600 | KM |  | Over Head Service Reservoir: per litre |  | 8 | 100 | 918 | standard methods. If decadal growth is assigned for future
| Distribution laid |  |  | 285 | KM |  | Clear Water Reservoir: per litre |  | 3 | 150 | 1395 | then it should be given in decadal growth
| Pumping Hours |  |  | 23 | Hours |  | NRW reduction and Replace Service Lines: per connection |  | 6000 | 200 | 1540 | 5 Demand Projection: Water demand has been taken 135 LPCD if population less
| Clear Water Reservoirs: At present: nos |  |  | 4 | Nos |  | Electric Connection on CWPS, RWPS & WTP |  | 21600000 | 250 | 2005 | than 1000000 else 160 LPCD as per Manual. Initial losses has been taken as
| Clear Water Reservoirs: Present Capacity |  |  | 6.75 | ML |  | Water Meter supply, installation & Maintenance 5 years |  | 2000 | 300 | 2543 | given in Input data and it remain same for next 5 years and then decrease by
| Distribution Reservoirs: at present: nos |  |  | 7 | Nos |  | CWPS with civil, mechanical & electrical complete, per KW |  | 25000 | 350 | 3197 | 10% every decade till minimum of 15 %, Fire demand taken as per manual
| Distribution Reservoirs: present Capacity |  |  | 2.65 | ML |  | Average Cost of rising main CWPS to OHSRs |  | 8000 | 400 | 3833 | The existing supply taken from input data and in future existing supply reduced
| Required capacity of OHSRs (20 to 35%) |  |  | 30 | % |  | Distribution extension n improvement, per capita of 2021 pop |  | 370 | 450 | 4547 | as per % reduction stared in input data, requirement -existing source=demand
| Required capacity of CWRs, |  | Detention time | 2 | Hours |  | Water Treatment Plant, Rate per MLD |  | 2500000 | 500 | 5325 | 6 Capacity of CWRs required: Requirement for year 15 and 30 years
| Avg. OHSR capacity |  |  | 1.75 | ML |  | Intake Arrangements, LS |  | 5000000 | 600 | 7015 | taken from water demand sheet, Storage norms taken from input sheet
| No of Distribution Zones |  |  | 38.3083 | Nos | IV | Additional Information for Surface Source |  |  | 700 | 9622 | 7 Rising main Design: template for rising Main design used to find
| Proposed staging of OHSRs |  |  | 20 | Meter |  | length of pipe Intake to WTP, m |  | 50 | 800 | 12550 | economical size of rising main
[7 empty] | Lowest water level in Intake, m |  | 233.5 | 900 | 15314 | 8 Raw Water Pumping Station: Head, discharge and Kilowatt calculated
| proposed water Colomn in OHSRs |  |  | 5.5 | Meter |  | Level of Inlet pipe in WTP/FSL in Inlet chamber, m |  | 240.1 | 1000 | 18354 | 9 Over Head Service Reservoir: Total Capacity worked out for 15/30 year DP
| Friction losses in specials, appurtenances |  |  | 10 | % |  | Design Period of pumping main, years |  | 30 |  |  | No of distribution zones and OHSRs found for year 15/30 years DP
| No of Working Pumps for RWPS |  |  | 4 | Nos |  | Efficiency of Pump set RWPS, % |  | 78 | Meter |  | 10 Clear Water Pumping Station: Head, discharge and Kilowatt calculated
| No of Working Pumps for CWPS |  |  | 2 | Nos |  | Efficiency of Pump set CWPS, % |  | 83 | Meter |  | 11 Estimate: Estimate has been worked out as per unit rates in input sheet
| Stand bye pumps |  |  | 50 | % |  | Length of R Main CWPS to OHSRs, per OHSR, m |  | 1400 | Meter |  | and quantities and sizes worked out in different sheets
| Energy Charges per Kilo Watt |  |  | 4.75 | Rs |  | Assumed losses in Rising Main & specials, meter/kilometer |  | 1 | Years |  | 12 WTP Capacity & Land required: WTP capacity and raw water requirement
| Intrest Rate |  |  | 10 | % |  | Minimum sump level below Ground level, meter |  | 4 | % |  | in phase 1 and in phase 2 calculated in Demand sheet
| rough ness coefficient for modified Hazen William |  |  | 1 | Cr |  | Ground level at CWPS, meters |  | 235 | %
| Proposed reduction in existing source,per 5 years |  |  | 25 | % |  | GL at OHSR site (maximum level ), meters |  | 236 | m
iii

## OUTPUT
Table 1: Projected Population & Water Demand
Year | Population | Gross Water Demand | Likely Deficit
|  | MLD | MLD
2011 | 499438 | 96.6286 | 15.5786
2016 | 591825.0318 | 114.2877 | 53.5002
2021 | 701302 | 125.7267 | 80.1361
2026 | 820406.9609 | 135.7702 | 101.5772
2031 | 959740 | 152.0976 | 126.4529
2036 | 1106087.919 | 194.126 | 174.8924
2041 | 1274752 | 223.4651 | 209.0399
Notes:
Gross Water Demand: Net water demand + losses
Deficit: Based on current supply levels and likely reduction in supply in future
Table 2: Source & Treatement Capacity
Particulars |  |  |  | Unit | Quantity/Value
Raw Water
Raw Water Requirement (Ultimate Design Year) |  |  |  | MLD | 220
WTP Capacity & Land Requirement
Ultimate Capacity Required (Ultimate Design Year) |  |  |  | MLD | 210
Land requirement for WTP ( including for CWR and RWPS/CWPS) |  |  |  | ha | 13
WTP Development Stages
Stage-1 development (in base year for intermediate design period |  |  |  | MLD | 102
Stage-2 development (in intermediate year for ultimate design period) |  |  |  | MLD | 108
Notes:
Table 3: Raw Water & Clear Water Pumping Requirements
Particulars |  |  |  | Unit | Quantity/Value
Raw Water Pumping Station
No of working pumps |  |  |  | No,s | 4
No of Standby pumps |  |  |  | No,s | 2
Pumping Hours |  |  |  | hours | 23
Discharge per pump, with respect to pumping hours |  |  |  | LPS | 296
Total Pumping Head |  |  |  | m | 7
Pump kilowatt |  |  |  | KW | 30
Total No of Pumps |  |  |  | No,s | 6
Total Kilowatt |  |  |  | KW | 180
Clear Water Pumping Station
No of working pumps |  |  |  | no,s | 2
No of Standby pumps |  |  |  | no,s | 1
Pumping Hours |  |  |  | hours | 23
Discharge per pump, with respect to pumping hours |  |  |  | LPS | 616
Total Pumping Head |  |  |  | m | 83.7
Pump kilowatt |  |  |  | KW | 680
Total No of Pumps |  |  |  | no,s | 3
Total Kilowatt |  |  |  | KW | 2040
Notes:
Table 4: Raw Water & Clear Water Rising Mains
Particulars |  |  |  | Unit | Quantity/Value
Raw Water Pumping Main (From Source to WTP)
Length |  |  |  | m | 50
Diameter |  |  |  | mm | 600
Recommended Type of Pipe |  |  |  |  | DI K7
Clear Water Pumping Main (From WTP to Zonal OHSRs)
Total Number of Zones |  |  |  | No,s | 38
Total Number of Zonal OHSRs (one per each Zone) |  |  |  | No,s | 38
Total length of Pipeline (for all zones) |  |  |  | m | 53200
Diameter
Recommended Type of Pipe |  |  |  |  | DI K7
Notes:
Table 5: Storage Requirement
Particulars |  |  |  | Unit | Quantity/Value
Clear Water Reservoir (CWR) at WTP
Ultimate Capacity Required (Ultimate Design Year) |  |  |  | ML | 16.2943
Available CWR Capacity |  |  |  | ML | 6.75
Total Capacity to be Developed |  |  |  | ML | 9.5443
CWR Development Stages
Stage-1 development (in base year for intermediate design period |  |  |  | ML | 4.5642
Stage-2 development (in intermediate year for ultimate design period) |  |  |  | ML | 4.9801
Over Head Service Reservoirs (OHSRs)
Total Storage Requirement of OHSRs |  |  |  | ML | 67.0395
Available OHSR Capacity |  |  |  | ML | 2.65
Total OHSR Capacity to be Development |  |  |  | ML | 64.3895
Total Number of Zones |  |  |  | No,s | 38
Recommeded Average Capacity of OHSR |  |  |  | ML | 1.75
OHSR Development Stages
Stage-1 development (in base year for intermediate design period
Storage Capacity to be Developed |  |  |  | ML | 38.0811
Zones to be Developed |  |  |  | No,s | 23
Total number of zonal OHSRs required |  |  |  | No,s | 23
Stage-2 development (in intermediate year for ultimate design period)
Storage Capacity to be Developed |  |  |  | ML | 26.3085
Zones to be Developed |  |  |  | No,s | 15
Total number of zonal OHSRs required |  |  |  | No,s | 15

## Pop_Projection
Table 1: Population Projection
Year | Population | Decadal Growth Rate | Annual Growth Rate | Households | HH Size
1951 | 54981
1961 | 67026 | 21.91% | 2.001%
1971 | 87981 | 31.26% | 2.758%
1981 | 137927 | 56.77% | 4.599%
1991 | 191000 | 38.48% | 3.309%
2001 | 261740 | 37.04% | 3.201% | 52000 | 5.0335
2011 | 499438 | 90.81% | 6.675% | 99223.5654 | 5.0335
2016 | 591825.0318 | 40.42% | 3.453% | 117578.1373 | 5.0335
2021 | 701302 | 40.42% | 3.453% | 139327.9743 | 5.0335
2026 | 820406.9609 | 36.85% | 3.187% | 162990.6089 | 5.0335
2031 | 959740 | 36.85% | 3.187% | 190671.9645 | 5.0335
2036 | 1106087.919 | 32.82% | 2.879% | 219746.9695 | 5.0335
2041 | 1274752 | 32.82% | 2.879% | 253255.536 | 5.0335
Population Projections
|  | Arithmetic Growth Method (AM) | Incremental Increase (IM) | Geometric Growth Method (GM) | Average of AM_IM_GM | Available Projected Data | Growth Rate based Projection | Input Growth Rate
Year | Population
1951 | 54981
1961 | 67026 | 12045 |  | 21.91%
1971 | 87981 | 20955 | 8910 | 31.26%
1981 | 137927 | 49946 | 28991 | 56.77%
1991 | 191000 | 53073 | 3127 | 38.48%
2001 | 261740 | 70740 | 17667 | 37.04%
|  | 41351.8 | 14673.75 | 37.09%
2011 | 499438 | 303091.8 | 317765.55 | 358822.6797 | 326560.0099 | 499438 | 261740 | 0%
2021 | 701302 | 344443.6 | 359117.35 | 491914.5543 | 398491.8348 | 701302 | 261740 | 0%
2031 | 959740 | 385795.4 | 400469.15 | 674371.8901 | 486878.8134 | 959740 | 261740 | 0%
2041 | 1274752 | 427147.2 | 441820.95 | 924504.9618 | 597824.3706 | 1274752 | 261740 | 0%
|  | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE

## Demand
Table 2: Water Demand
Year | Population | LPCD | Losses | Demand | Losses | Fire Demand | Total | Present | Deficit
|  |  | % | MLD | MLD | MLD | MLD | MLD | MLD
2011 | 499438 | 135 | 40 | 67.4241 | 26.9697 | 2.2348 | 96.6286 | 81.05 | 15.5786
2016 | 591825.0318 | 135 | 40 | 79.8964 | 31.9586 | 2.4327 | 114.2877 | 60.7875 | 53.5002
2021 | 701302 | 135 | 30 | 94.6758 | 28.4027 | 2.6482 | 125.7267 | 45.5906 | 80.1361
2026 | 820406.9609 | 135 | 20 | 110.7549 | 22.151 | 2.8643 | 135.7702 | 34.193 | 101.5772
2031 | 959740 | 135 | 15 | 129.5649 | 19.4347 | 3.098 | 152.0976 | 25.6447 | 126.4529
2036 | 1106087.919 | 150 | 15 | 165.9132 | 24.887 | 3.3258 | 194.126 | 19.2335 | 174.8924
2041 | 1274752 | 150 | 15 | 191.2128 | 28.6819 | 3.5704 | 223.4651 | 14.4252 | 209.0399
Table 3: WTP Capacity Requirement
Parameter | [7 empty] | Units | Quantity
Considering 5% treatment losses, requirement for 15 yr DP | [7 empty] | MLD | 106.6561
Ultimate WTP Capacity Required (30 years design period) | [7 empty] | MLD | 210
Land requirement for WTP ( including for CWR and RWPS/CWPS) | [7 empty] | ha | 13 | @ | 625 | m2 per MLD
Proposed development of WTP - 2 stage (Intermediate - 15 year and ultimate - 30 years)
WTP Capacity (Stage-1 development in base year for intermediate design period) | [7 empty] | MLD | 102
WTP Capacity (Stage-2 development in intermediate year for ultimate design period) | [7 empty] | MLD | 108
Raw Water Requirement (Ultimate Demand + 5% WTP losses) | [7 empty] | MLD | 220

## CWRs
Table 2: Clear Water Reservoirs
year | Demand | Capacity Reqd | Available Capacity | Proposed Capacity
| MLD | ML | ML | ML
2026 | 135.7702 | 11.3142 | 6.75 | 4.5642
2041 | 223.4651 | 16.2943 | 6.75 | 9.5443

## RWPS
Table 3: Raw Water Pumping Station
Description | Unit | Quantity
Minimum water level in Intake |  | 233.5
Outlet level |  | 240.1
Static head |  | 6.6
Friction Losses in pipe line |  | 0.010288
Losses in specials,entry,exit,piping |  | 0.0010288
Total Pumping Head | m | 6.6113
Rounding upwards | m | 7
Quantity of water to be pumped | MLD | 102
No of working pumps | No,s | 4
No of Standby pumps | No,s | 2
Rounding upwards | No,s | 2
Pumping Hours | hours | 23
Discharge per pump, with respect to pumping hours | MLD | 24.4375
As above | LPS | 295.1389
Pump Efficiency | % | 78
Pump kilowatt | KW | 25.9675
Motor Rating coefficient |  | 1.15
Motor Rating |  | 29.8626
Round up |  | 30
Total No of Pumps | No,s | 6
Total Kilowatt | KW | 180

## OHSRs
Table 4: Over Head Service Reservoirs
year | Demand | OHSRs Capacity | Present Capacuty | New OHSRs
| MLD | ML | ML | ML
2026 | 135.7702 | 40.7311 | 2.65 | 38.0811
2041 | 223.4651 | 67.0395 | 2.65 | 64.3895
Recommeded Average Capacity of OHSR |  |  |  |  | 1.75 | ML
Number of Zones Required (Intermediate Year) |  |  |  |  | 23 | No,s
Number of Zones Required (Ultimate Year) |  |  |  |  | 38 | No,s
Number of OHSR per zone |  |  |  |  | 1 | No,s
Total number of zonal OHSRs (intermediate year) |  |  |  |  | 23 | No,s
Total number of zonal OHSRs (Ultimate Year) |  |  |  |  | 38 | No,s

## Estimate
Table 7: Estimate
S No | Item | Quantity | Rate | Units | Amount
Rs
1 | Construction of Intake arrangements | 1 | 5000000 | No | 5000000
2 | Construction of Raw Water Pump House | 180 | 25000 | KiloWatt | 4500000
3 | Construction of Water Treatment Plant | 210 | 2500000 | MLD | 525000000
4 | Construction of CWRs | 9544329.2552 | 3 | Litre | 28632987.7655
5 | Construction of OHSRs | 64389526.0784 | 8 | Litre | 515116208.627
6 | Clear Water Pumping Station | 2040 | 25000 | KW | 51000000
7 | R Main RWPS to WTP DI Pipe K7, Dia in mm
| 600 | 50 | 10522.5 | meter | 526125
8 | R Main CWPS to Zonal Service Reservoirs | 53200 | 8000 | meter | 425600000
9 | Distribution system | 1274752 | 370 | Nos | 471658240
10 | Domestic Meters | 30034 | 2000 | Nos | 60068000
11 | Reduction of NRW & Replace Service Line | 30034 | 6000 | Nos | 180204000
12 | Electric Connection on CWPS, RWPS,WTP | 1 | 21600000 | Nos | 21600000
13 | Cost of Land for WTP, CWPS, RWPS, SRs | 1 | 10000000 |  | 10000000
| Sub Total |  |  |  | 2298905561.3925
| Physical Contingency | 10% |  |  | 229890556.1392
| Other contingencies | 5% |  |  | 114945278.0696
| Grand Total |  |  |  | 2643741395.6014

## RM Design 1
CALCULATION OF LEAST-COST PIPE SIZE
[5 empty] | PUMPING TRANSMISSION MAIN | Intake to WTP
| ECONOMACAL SIZE OF RAW WATER RISING MAIN MAIN | [7 empty] | I N P U T | D A T A
| From : | Intake |  |  | ===== | = | = | = | = | = | = | =
| To : | WTP
| 1) Water requirement : |  |  |  | Year | Peak Discharge
P I P E D A T A
| A. | Initial |  |  | 2011 | 15.5786 | mld | DIAMETER | MATERIAL | CLASS | Cr | RATE Rs/m
| B. | Intermediate |  |  | 2026 | 107.1 | mld | 100 | DI | K7 | 1 | 918
| C. | Ultimate |  |  | 2041 | 220 | mld | 150 | DI | K7 | 1 | 1395
[8 empty] | 200 | DI | K7 | 1 | 1540
| 2) Pumping main |  |  |  | LENGTH | 50 | M | 250 | DI | K7 | 1 | 2005
| 3) Static head for pump |  |  |  | ST.HEAD | 6.6 | M | 300 | DI | K7 | 1 | 2543
| 4) Design period |  |  |  | YEAR | 30 | yr. | 350 | DI | K7 | 1 | 3197
| 5) Combined eff. of pump set |  |  |  | EFF. % | 78 | % | 400 | DI | K7 | 1 | 3833
| 6) Cost of pumping unit |  |  |  | Rs./KW | 25000 | Rs | 450 | DI | K7 | 1 | 4547
| 7) Interest rate |  |  |  | INTEREST | 10 | % | 500 | DI | K7 | 1 | 5325
| 8) Life of electric motor & pump set |  |  |  | P.Yrs | 15 | yr. | 600 | DI | K7 | 1 | 7015
| 9) Energy charges per kWh |  |  |  | P/KWH | 4.75 | Rs | 700 | DI | K7 | 1 | 9622
| 10) Pumping hours for discharge |  |  |  | PUMPING- | 23 | hrs | 800 | DI | K7 | 1 | 12550
|  |  | at the end of 30 years |  | HOURS |  |  | 900 | DI | K7 | 1 | 15314
| 11Energy Charges capitalised:Cc |  |  |  | n | 15 | years | 1000 | DI | K7 | 1 | 18354
| cr((1-(1+r)^(-n))/n) |  |  |  | Rate of intrest | 0.1
[5 empty] | cc | 7.6061 | *Cr
| 12 Present value of investment reqd after 15 years=C/((1+r)^n) |  |  |  | C | 4.1772 | *Po
PRESS <ALT>M for MENU
CALCULATIONS: | [5 empty] | 1st 15 years |  | 2nd 15 years
| 1) Discharge at Start OF PERIOD |  |  |  |  | 15.5786 | mld | 107.1 | mld
| 2) Discharge at the end of 15 yrs |  |  |  |  | 107.1 | mld | 220 | mld
| 3) Average Discharge |  |  |  |  | 61.3393 | mld | 163.55 | mld
| 4) Ave.pumping hours during the period |  |  |  |  | 13.1728 | hrs | 17.0984 | hrs
| 5) KW required at combined |  |  |  |  | 16.2579 | * H1 | 33.3962 | * H2
efficiency of pumping set
6) Ave.annual charges for electrical
| energy Rs. |  |  |  |  | 371556.9161 | *H1 | 990688.4676 | * H2
Modified Hazen William's Formula
[5 empty] | V= | 143.534CR r0.6575 S0.5525
[5 empty] | h= | [L(Q/CR)1.81 ]/[994.62D4.81]
Friction Head Loss (First 15 years)
Dia. in mm | L | Q | CR | Q/CR | (Q/CR)^1.81 | 994.62 | D | D^4.81 | h( First 15 yrs)
100 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.1 | 1.5488e-05 | 56.9157
150 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.15 | 0.00010889 | 8.0953
200 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.2 | 0.00043446 | 2.029
250 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.25 | 0.0012708 | 0.69365
300 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.3 | 0.0030546 | 0.28859
350 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.35 | 0.0064116 | 0.13749
400 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.4 | 0.012187 | 0.072331
450 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.45 | 0.021476 | 0.041047
500 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.5 | 0.035649 | 0.024728
600 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.6 | 0.085686 | 0.010288
700 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.7 | 0.17985 | 0.0049013
800 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.8 | 0.34187 | 0.0025785
900 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 0.9 | 0.60243 | 0.0014633
1000 | 50 | 0.1071 | 1 | 0.1071 | 0.017536 | 994.62 | 1 | 1 | 0.00088152
Velocity
Dia. in mm | 143.534 | CR | r=A/P=D/4 | r0.6575 | S | S^0.5525 | V
100 | 143.534 | 1 | 0.025 | 0.088439 | 1.1383 | 1.0742 | 13.6359
150 | 143.534 | 1 | 0.0375 | 0.11546 | 0.16191 | 0.36569 | 6.0604
200 | 143.534 | 1 | 0.05 | 0.1395 | 0.04058 | 0.17025 | 3.4089
250 | 143.534 | 1 | 0.0625 | 0.16154 | 0.013873 | 0.094091 | 2.1817
300 | 143.534 | 1 | 0.075 | 0.18212 | 0.0057718 | 0.057959 | 1.5151
350 | 143.534 | 1 | 0.0875 | 0.20154 | 0.0027498 | 0.038478 | 1.1131
400 | 143.534 | 1 | 0.1 | 0.22004 | 0.0014466 | 0.026983 | 0.85222
450 | 143.534 | 1 | 0.1125 | 0.23776 | 0.00082094 | 0.019731 | 0.67335
500 | 143.534 | 1 | 0.125 | 0.25481 | 0.00049456 | 0.014913 | 0.54542
600 | 143.534 | 1 | 0.15 | 0.28726 | 0.00020576 | 0.009186 | 0.37876
700 | 143.534 | 1 | 0.175 | 0.31791 | 9.8026e-05 | 0.0060984 | 0.27827
800 | 143.534 | 1 | 0.2 | 0.34708 | 5.157e-05 | 0.0042766 | 0.21305
900 | 143.534 | 1 | 0.225 | 0.37502 | 2.9265e-05 | 0.0031272 | 0.16834
1000 | 143.534 | 1 | 0.25 | 0.40193 | 1.763e-05 | 0.0023635 | 0.13635
Friction Head Loss (Second 15 years)
Dia. in mm | L | Q | CR | Q/CR | (Q/CR)^1.81 | 994.62 | D | D^4.81 | h( Second 15 yrs)
100 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.1 | 1.5488e-05 | 209.4584
150 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.15 | 0.00010889 | 29.7919
200 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.2 | 0.00043446 | 7.467
250 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.25 | 0.0012708 | 2.5527
300 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.3 | 0.0030546 | 1.062
350 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.35 | 0.0064116 | 0.50598
400 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.4 | 0.012187 | 0.26619
450 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.45 | 0.021476 | 0.15106
500 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.5 | 0.035649 | 0.091002
600 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.6 | 0.085686 | 0.037861
700 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.7 | 0.17985 | 0.018037
800 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.8 | 0.34187 | 0.0094893
900 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 0.9 | 0.60243 | 0.0053851
1000 | 50 | 0.22 | 1 | 0.22 | 0.064533 | 994.62 | 1 | 1 | 0.0032441
Velocity
Dia. in mm | 143.534 | CR | r=A/P=D/4 | r^0.6575 | S | S^0.5525 | V
100 | 143.534 | 1 | 0.025 | 0.088439 | 4.1892 | 2.2066 | 28.0108
150 | 143.534 | 1 | 0.0375 | 0.11546 | 0.59584 | 0.75121 | 12.4491
200 | 143.534 | 1 | 0.05 | 0.1395 | 0.14934 | 0.34973 | 7.0026
250 | 143.534 | 1 | 0.0625 | 0.16154 | 0.051055 | 0.19328 | 4.4816
300 | 143.534 | 1 | 0.075 | 0.18212 | 0.021241 | 0.11906 | 3.1122
350 | 143.534 | 1 | 0.0875 | 0.20154 | 0.01012 | 0.079041 | 2.2865
400 | 143.534 | 1 | 0.1 | 0.22004 | 0.0053238 | 0.055429 | 1.7506
450 | 143.534 | 1 | 0.1125 | 0.23776 | 0.0030212 | 0.040532 | 1.3832
500 | 143.534 | 1 | 0.125 | 0.25481 | 0.00182 | 0.030633 | 1.1204
600 | 143.534 | 1 | 0.15 | 0.28726 | 0.00075722 | 0.01887 | 0.77804
700 | 143.534 | 1 | 0.175 | 0.31791 | 0.00036075 | 0.012527 | 0.57162
800 | 143.534 | 1 | 0.2 | 0.34708 | 0.00018979 | 0.008785 | 0.43765
900 | 143.534 | 1 | 0.225 | 0.37502 | 0.0001077 | 0.006424 | 0.34579
1000 | 143.534 | 1 | 0.25 | 0.40193 | 6.4883e-05 | 0.0048551 | 0.28009
= | = | = | = | = | = | = | = | = | = | = | =
TABLE 1 - VELOCITY AND HEADLOSSES FOR DIFFERENT PIPE SIZES
- | - | - | - | - | - | - | - | - | - | - | -
[7 empty] | Total head(m) for |  | 50 | m length
Sl. | Pipe | Frictional Head |  | Velocity in |  |  | including | 6.6 | m static head
No. | Size | loss per |  | m/s |  | ------ | --------- | --------- | --------- | --------- | ---------
| in | 1000 m |  |  |  | 1st stage flow |  |  | 2nd stage flow
| mm | ---------------- |  | -------------- |  | ------- | --------- | -------- | ------- | --------- | ---------
|  | 1st | 2nd | 1st | 2nd | Frict- |  | Total | Frict- |  | Total
|  | stage | stage | stage | stage | ional | Other* | Head | ional | Other* | Head
|  | flow | flow | flow | flow | loss | losses | H1 | loss | losses | H2
- | - | - | - | - | - | - | - | - | - | - | -
1 | 100 | 1138.3132 | 4189.1688 | 13.6359 | 28.0108 | 56.9157 | 5.6916 | 69.2072 | 209.4584 | 20.9458 | 237.0043
2 | 150 | 161.9059 | 595.839 | 6.0604 | 12.4491 | 8.0953 | 0.80953 | 15.5048 | 29.7919 | 2.9792 | 39.3711
3 | 200 | 40.5796 | 149.3391 | 3.4089 | 7.0026 | 2.029 | 0.2029 | 8.8319 | 7.467 | 0.7467 | 14.8137
4 | 250 | 13.873 | 51.0548 | 2.1817 | 4.4816 | 0.69365 | 0.069365 | 7.363 | 2.5527 | 0.25527 | 9.408
5 | 300 | 5.7718 | 21.241 | 1.5151 | 3.1122 | 0.28859 | 0.028859 | 6.9174 | 1.062 | 0.1062 | 7.7683
6 | 350 | 2.7498 | 10.1195 | 1.1131 | 2.2865 | 0.13749 | 0.013749 | 6.7512 | 0.50598 | 0.050598 | 7.1566
7 | 400 | 1.4466 | 5.3238 | 0.85222 | 1.7506 | 0.072331 | 0.0072331 | 6.6796 | 0.26619 | 0.026619 | 6.8928
8 | 450 | 0.82094 | 3.0212 | 0.67335 | 1.3832 | 0.041047 | 0.0041047 | 6.6452 | 0.15106 | 0.015106 | 6.7662
9 | 500 | 0.49456 | 1.82 | 0.54542 | 1.1204 | 0.024728 | 0.0024728 | 6.6272 | 0.091002 | 0.0091002 | 6.7001
10 | 600 | 0.20576 | 0.75722 | 0.37876 | 0.77804 | 0.010288 | 0.0010288 | 6.6113 | 0.037861 | 0.0037861 | 6.6416
11 | 700 | 0.098026 | 0.36075 | 0.27827 | 0.57162 | 0.0049013 | 0.00049013 | 6.6054 | 0.018037 | 0.0018037 | 6.6198
12 | 800 | 0.05157 | 0.18979 | 0.21305 | 0.43765 | 0.0025785 | 0.00025785 | 6.6028 | 0.0094893 | 0.00094893 | 6.6104
13 | 900 | 0.029265 | 0.1077 | 0.16834 | 0.34579 | 0.0014633 | 0.00014633 | 6.6016 | 0.0053851 | 0.00053851 | 6.6059
14 | 1000 | 0.01763 | 0.064883 | 0.13635 | 0.28009 | 0.00088152 | 8.8152e-05 | 6.601 | 0.0032441 | 0.00032441 | 6.6036
- | >>> * Other losses = 10% of frictional loss
= | = | = | = | = | = | = | = | = | = | = | =
TABLE 2 - KILOWATTS & COST OF PUMP SETS REQUIRED FOR DIFFERENT PIPE SIZES AND PIPE COST
- | - | - | - | - | - | - | - | - | - | - | -
|  |  | 1st stage flow of |  |  |  | 2nd stage flow of |  |  | Cost | Cost
| 61.3393 |  |  | million liters/day |  |  | 163.55 | MLD |  | of | of
|  |  | -------- | --------- | --------- |  | -------- | --------- | --------- | pipe | 50
Sl. | PIPE | Class | H1 | Kw | Pump |  | H2 | Kw | Pump | per | meter
No. | Size | of | Total | req'd | Cost @ Rs |  | Total | req'd | Cost @ Rs | unit | pipe
| in | PIPE | head | plus 50% | 25000 |  | head | plus % | 25000 | length | line
| mm |  | in |  | per kw |  | in | 50 | per kw |  | THS
|  |  | meters | standby | Rs THS |  | meters | standby | Rs THS | ( Rs ) | ( Rs )
- | - | - | - | - | - | - | - | - | - | - | -
1 | 100 | K7 | 69.2072 | 1687.7458 | 42193.6458 |  | 237.0043 | 11872.5779 | 296814.4482 | 918 | 45.9
2 | 150 | K7 | 15.5048 | 378.1138 | 9452.8454 |  | 39.3711 | 1972.2722 | 49306.8057 | 1395 | 69.75
3 | 200 | K7 | 8.8319 | 215.3816 | 5384.5401 |  | 14.8137 | 742.0804 | 18552.0097 | 1540 | 77
4 | 250 | K7 | 7.363 | 179.5607 | 4489.0176 |  | 9.408 | 471.2884 | 11782.2096 | 2005 | 100.25
5 | 300 | K7 | 6.9174 | 168.6947 | 4217.3677 |  | 7.7683 | 389.1457 | 9728.6429 | 2543 | 127.15
6 | 350 | K7 | 6.7512 | 164.6414 | 4116.0341 |  | 7.1566 | 358.504 | 8962.6003 | 3197 | 159.85
7 | 400 | K7 | 6.6796 | 162.8935 | 4072.3372 |  | 6.8928 | 345.2908 | 8632.2693 | 3833 | 159.85
8 | 450 | K7 | 6.6452 | 162.0543 | 4051.357 |  | 6.7662 | 338.9467 | 8473.667 | 4547 | 227.35
9 | 500 | K7 | 6.6272 | 161.6165 | 4040.4129 |  | 6.7001 | 335.6373 | 8390.9336 | 5325 | 266.25
10 | 600 | K7 | 6.6113 | 161.2292 | 4030.7289 |  | 6.6416 | 332.709 | 8317.7262 | 7015 | 350.75
11 | 700 | K7 | 6.6054 | 161.0847 | 4027.1164 |  | 6.6198 | 331.6167 | 8290.4177 | 9622 | 481.1
12 | 800 | K7 | 6.6028 | 161.0223 | 4025.5587 |  | 6.6104 | 331.1457 | 8278.6418 | 12550 | 627.5
13 | 900 | K7 | 6.6016 | 160.9924 | 4024.8108 |  | 6.6059 | 330.9195 | 8272.9878 | 15314 | 765.7
14 | 1000 | K7 | 6.601 | 160.9768 | 4024.4206 |  | 6.6036 | 330.8015 | 8270.0384 | 18354 | 917.7
TABLE 3 - COMPARATIVE STATEMENT OF OVERALL COST OF PUMPING MAIN FOR DIFFERENT PIPE SIZES
- | - | - | - | - | - | - | - | - | - | - | -
| 1st stage flow |  | 61.3393 | mld | 2nd stage flow |  | 163.55 | mld
| ------ | --------- | --------- | --------- | ------ | --------- | --------- | --------- |  |  | GRAND
TOTAL
of
| Cost | Annual | Capital- | Capital- | Cost | Annual | Capital- | Capital- | Initial | PIPE | Capital-
| of | Energy | ised | ised | of | Energy | ised | ised | Capital | SIZE | ised
Sl. | pump | Charges | Energy | Total | pump | Charges | Energy | Total | Investment | in | cost
No. | sets |  | Charges | Cost | sets |  | Charges | Cost | for pumpsets | (mm) | for
& annual ele
[9 empty] | ct. Charges |  | 30 yrs
| THS | THS | THS | THS | THS | THS | THS | THS | THS |  | THS | Dia
1 | 42193.6458 | 25714.4225 | 195585.9421 | 237779.588 | 296814.4482 | 234797.4131 | 1785887.7917 | 2082702.2399 | 498582.3574 | 100 | 736407.8454 | 100
2 | 9452.8454 | 5760.9257 | 43818.059 | 53270.9044 | 49306.8057 | 39004.538 | 296671.617 | 345978.4227 | 82824.4836 | 150 | 136165.138 | 150
3 | 5384.5401 | 3281.5448 | 24959.6907 | 30344.2308 | 18552.0097 | 14675.7138 | 111624.6456 | 130176.6553 | 31163.2563 | 200 | 61584.4871 | 200
4 | 4489.0176 | 2735.7791 | 20808.5533 | 25297.5709 | 11782.2096 | 9320.41 | 70891.7793 | 82673.9889 | 19791.4956 | 250 | 45189.3165 | 250
5 | 4217.3677 | 2570.2253 | 19549.3377 | 23766.7054 | 9728.6429 | 7695.9198 | 58535.7776 | 68264.4205 | 16341.9595 | 300 | 40235.815 | 300
6 | 4116.0341 | 2508.4687 | 19079.6122 | 23195.6463 | 8962.6003 | 7089.9358 | 53926.6151 | 62889.2155 | 15055.1782 | 350 | 38410.6745 | 350
7 | 4072.3372 | 2481.8382 | 18877.0583 | 22949.3955 | 8632.2693 | 6828.6248 | 51939.0629 | 60571.3321 | 14500.2953 | 400 | 37609.5409 | 400
8 | 4051.357 | 2469.052 | 18779.8058 | 22831.1628 | 8473.667 | 6703.1612 | 50984.7769 | 59458.4439 | 14233.8787 | 450 | 37292.3916 | 450
9 | 4040.4129 | 2462.3822 | 18729.075 | 22769.4878 | 8390.9336 | 6637.7143 | 50486.9824 | 58877.9159 | 14094.905 | 500 | 37130.6428 | 500
10 | 4030.7289 | 2456.4804 | 18684.1854 | 22714.9142 | 8317.7262 | 6579.803 | 50046.5049 | 58364.2312 | 13971.9329 | 600 | 37037.5971 | 600
11 | 4027.1164 | 2454.2789 | 18667.4402 | 22694.5566 | 8290.4177 | 6558.2004 | 49882.1935 | 58172.6112 | 13926.0606 | 700 | 37101.7172 | 700
12 | 4025.5587 | 2453.3295 | 18660.2194 | 22685.778 | 8278.6418 | 6548.8849 | 49811.3395 | 58089.9813 | 13906.2797 | 800 | 37219.5577 | 800
13 | 4024.8108 | 2452.8737 | 18656.7524 | 22681.5632 | 8272.9878 | 6544.4123 | 49777.3203 | 58050.3081 | 13896.7822 | 900 | 37344.0454 | 900
14 | 4024.4206 | 2452.6359 | 18654.9439 | 22679.3645 | 8270.0384 | 6542.0792 | 49759.5745 | 58029.6129 | 13891.828 | 1000 | 37488.8925 | 1000
[5 empty] | Minimum capitalised cost |  | 37037.5971 | thousand Rs
[5 empty] | Economical Dia |  | 600 | mm
[5 empty] | frictional Losses in pipe line, economical dia,15year DP |  | 0.010288 | m
[5 empty] | Total length of pipe |  | 50 | m
[5 empty] | Type of Pipe |  | DI K7

## CWPS
Table 8: Clear Water Pumping Station
Parameter | Units | Quantity
Staging Height of Service Reservoir | m | 20
Water Colomn in Service Reservoir | m | 5.5
No of Distribution zones | No | 38
Length of Rising Main | m | 53200
Friction Losses in pipes and specials | m | 53.2
Suction Head | m | 4
difference in level in CWPS and OHSR | m | 1
Total Pumping Head | m | 83.7
Rounding | m | 84
No of stand working pumps |  | 2
Total quantity of water to be pumped | MLD | 102
Pumping Hours | hours | 23
Pump Discharge | LPS | 615.942
Rounding | LPS | 616
Pump Kilo Watt |  | 611.1977
Multiplying Coefficient for KW |  | 1.1
Motor Kilo Watt |  | 672.3175
Rounding , upward multiple of 10 | KW | 680
Stand bye pumps | no,s | 1
Total No of Pumps | no,s | 3
Total kilo Watt installed | KW | 2040