## INPUT DATA
Template for Deign and Estimation of Sewerage System | [8 empty] | City | Hapur
Input Data | [5 empty] | Assumptions | [5 empty] | User Instructions
I | Population | [10 empty] | 1 Input Data:The cells for data input and requiring users review are shaded with different
| Year | Population | Households |  |  |  |  | Method/Basis |  |  |  | colours. Input data or review the data/result according to following color codes:
| 1951 | 49260 |  |  |  | I | Population Projections | Geometric Growth Method (GM) | Choose from drop down menu only
| 1961 | 55248 | [10 empty] | Input data to be provided | Enter data if condition satisfy
| 1971 | 71266 |  |  |  |  | If the above option is "Available Projected Data" enter projected population below
| 1981 | 102837 |  |  |  |  | Year | 2011 | 2021 | 2031 | 2041 |  | Review the provided values & | No value to be entered
| 1991 | 146262 |  |  |  |  | Population | 310000 | 400000 | 500000 | 600000 |  | revise/update if required | Calculates automatically
| 2001 | 211893 | 31174 | [9 empty] | No data to be entered select from drop down menu
[7 empty] | If the above option is "Growth Rate based Project" enter below the Decadal Growth Rate to be used for Projection |  |  |  |  | 2 Output:3 output tables are given which is final output and shall be part of report
[7 empty] | Decade | Decadal Growth Rate |  |  |  | 4 Population Projection: Excle sheet gives population projection by different
II | Present Sewerage System | [5 empty] | Decade | 2001-11 | 2011-21 | 2021-31 | 2031-41 | standard methods. If decadal growth is assigned for future
| Present Population |  | 2010 | 275000 | Nos |  | Growth Rate% | 2% | 1.9% | 1.8% | 1.7% | then it should be given in decadal growth
| Sewage disposal through sewers |  |  |  | MLD | [6 empty] | 5 Sewage Pumping Station: Three SPS required in this case. In case of more or less suitably it is to be corrected. Yellow cells should be filled suitably and
| No of Sewer connections |  |  |  | Nos | II | Design Period |  |  |  |  | green cells should be reviewed and modified/updated as per need
| Coverage with sewer network |  |  |  | Persons |  | Base Year | Year |  | 2011
| Length of Gravity Sewer Network |  |  | 15 | KM |  | Design Period for STP | No. of Years: Choose from drop down | 15 | 2026
| No of Sewage Pumping Stations |  |  | 1
| STP Design Capacity |  |  | 0 | MLD | III | Market Rates |  | Rs | DI K7 Dia in mm | Rs/meter
| STP Actual Flow |  |  | 0 | MLD |  | Sewer Network per KM |  | 5500000 | 100 | 918
| No of Employees for sewerage |  |  |  | Nos |  | SPS with civil, M & E complete, per MLD |  | 25000 | 150 | 1395
| Road Length Pucca |  |  | 150 | KM |  | SewageTreatment Plant, Rate per MLD |  | 7000000 | 200 | 1540
| Road Length Kutcha |  |  | 70 | KM |  | Land Cost per Hectare |  | 10000000 | 250 | 2005
| No of STPs at present |  |  | 0 |  |  |  | DI K7 Dia in mm | Rs/meter | 300 | 2543
| Waste Water qty reaching sewers |  |  | 80% |  |  |  | 700 | 9622 | 350 | 3197
| Land Required |  | ASP | 0.2 | Ha/MLD |  |  | 800 | 12550 | 400 | 3833
| STP capacity to develop in stages |  |  | 2 | Stages |  |  | 900 | 15314 | 450 | 4547
| Qty of waste from other sources |  |  | 5 | MLD |  |  | 1000 | 18354 | 500 | 5325
| Ground Water Infiltration |  |  | 5000 | LPD/Ha |  | Length of Sewer in meter per Hactare area of city |  | 125 | 600 | 7015
| Ground Water Table |  |  | 20 | m | IV | SPS Design |  | SPS1 | SPS2 | SPS3
| Area of Municipal Council |  |  | 14.2 | ha |  | Peak Sewage flow | lps | 43.7 | 81.69 | 1173.11
| Area of Master Plan Area, 2031 |  |  | 46.5 | ha |  | Peak factor |  | 3 | 2.5 | 2.25
[7 empty] | Liquid depth in wet well assumed | m | 2.2 | 2.2 | 2.2
[7 empty] | Invert Level | m | 207.5 | 207.5 | 202.76
[7 empty] | Ground Level | m | 211 | 211 | 207
[7 empty] | Delivery length of pumping Main | m | 150 | 150 | 600
[7 empty] | Level of Delivery Point above GL of SPS | m | 7 | 7 | 7.5
[7 empty] | Detention time in Wetwell | mins | 20 | 20 | 20
[7 empty] | Velocity of flow during peak flow | m/s | 1.2 | 1.2 | 1.2
[7 empty] | Velocity of flow during average flow | m/s | 0.8 | 0.8 | 0.8
[7 empty] | Proposed pumps Working | numbers | 2 | 2 | 2
[7 empty] | Stand by pumps |  | 100% | 100% | 100%
[7 empty] | Material of pumping Main pipe |  | DI | DI | DI

## OUTPUT
Table 1: Projected Population & Water Demand
Year | Population | Waste Generation
MLD
2011 | 285016.5431 | 35.7818
2016 | 330557.3342 | 40.7002
2021 | 383374.7685 | 46.4045
2026 | 444631.5296 | 53.0202
2031 | 515676.0781 | 60.693
2036 | 598072.336 | 69.5918
2041 | 693634.1131 | 79.9125
Table 2: Sewage Treatment Treatement Capacity
Ultimate STP Capacity Required (30 years design period) |  |  |  | MLD | 79.9125
Existing Capacity of STPs |  |  |  | MLD | 0
STP capacity required to be developed now |  |  |  | MLD | 79.9125
Land requirement for STP |  |  |  | ha | 15.9825
STP capacity of 30 years to be developed in modules of equal capacity |  |  |  | No Modules | 2
STP capacity for Stage 1 |  |  |  | MLD | 39.9562
STP capacity for Stage 2 |  |  |  | MLD | 39.9562
Table 3: Sewage Pumping and Pumping Main
Particulars
Diameter of the wetwell |  | m | 3.5 | 5 | 19.5
Discharge in each Pump |  | cum/hr | 80 | 150 | 2120
Pumping Head |  | m | 11.5 | 11 | 173
KW required of each pump |  | KW | 6 | 11 | 144
No of Pumps |  | No | 4 | 4 | 4
Total KW |  | KW | 24 | 44 | 576
Diameter of the pipe proposed |  | mm | 200 | 270 | 1100
Pipe Material |  |  | DI K7 | DI K7 | DI K7

## Pop_Projection
Table 1: Population Projection
Year | Population | Decadal Growth Rate | Annual Growth Rate | Households | HH Size
1951 | 49260
1961 | 55248 | 12.16% | 1.154%
1971 | 71266 | 28.99% | 2.579%
1981 | 102837 | 44.3% | 3.735%
1991 | 146262 | 42.23% | 3.585%
2001 | 211893 | 44.87% | 3.776% | 31174 | 6.7971
2011 | 285016.5431 | 34.51% | 3.009% | 41932.0398 | 6.7971
2016 | 330557.3342 | 34.51% | 3.009% | 48632.0659 | 6.7971
2021 | 383374.7685 | 34.51% | 3.009% | 56402.6421 | 6.7971
2026 | 444631.5296 | 34.51% | 3.009% | 65414.824 | 6.7971
2031 | 515676.0781 | 34.51% | 3.009% | 75866.9992 | 6.7971
2036 | 598072.336 | 34.51% | 3.009% | 87989.254 | 6.7971
2041 | 693634.1131 | 34.51% | 3.009% | 102048.4388 | 6.7971
Population Projections
|  | Arithmetic Growth Method (AM) | Incremental Increase (IM) | Geometric Growth Method (GM) | Average of AM_IM_GM | Available Projected Data | Growth Rate based Projection | Input Growth Rate
Year | Population
1951 | 49260
1961 | 55248 | 5988 |  | 12.16%
1971 | 71266 | 16018 | 10030 | 28.99%
1981 | 102837 | 31571 | 15553 | 44.3%
1991 | 146262 | 43425 | 11854 | 42.23%
2001 | 211893 | 65631 | 22206 | 44.87%
|  | 32526.6 | 14910.75 | 34.51%
2011 | 285016.5431 | 244419.6 | 259330.35 | 285016.5431 | 262922.1644 | 310000 | 258296.3846 | 2%
2021 | 383374.7685 | 276946.2 | 291856.95 | 383374.7685 | 317392.6395 | 400000 | 374199.7852 | 1.9%
2031 | 515676.0781 | 309472.8 | 324383.55 | 515676.0781 | 383177.476 | 500000 | 478120.9473 | 1.8%
2041 | 693634.1131 | 341999.4 | 356910.15 | 693634.1131 | 464181.221 | 600000 | 591806.2312 | 1.7%
|  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE

## Waste Generation_STP
Table 2: Waste Water quantity Generation
Year | Population | LPCD | Waste Water | WW in Sewers | GW Infiltration | Qty other sources | Total
|  |  | MLD | MLD | MLD | MLD | MLD
2011 | 285016.5431 | 135 | 38.4772 | 30.7818 | 0 | 5 | 35.7818
2016 | 330557.3342 | 135 | 44.6252 | 35.7002 | 0 | 5 | 40.7002
2021 | 383374.7685 | 135 | 51.7556 | 41.4045 | 0 | 5 | 46.4045
2026 | 444631.5296 | 135 | 60.0253 | 48.0202 | 0 | 5 | 53.0202
2031 | 515676.0781 | 135 | 69.6163 | 55.693 | 0 | 5 | 60.693
2036 | 598072.336 | 135 | 80.7398 | 64.5918 | 0 | 5 | 69.5918
2041 | 693634.1131 | 135 | 93.6406 | 74.9125 | 0 | 5 | 79.9125
Table 3: STP Capacity Requirement
Parameter
Ultimate STP Capacity Required (30 years design period) | [5 empty] | MLD | 79.9125
Existing Capacity of STPs | [5 empty] | MLD | 0
STP capacity required to be developed now | [5 empty] | MLD | 79.9125
Land requirement for STP | [5 empty] | ha | 15.9825
STP capacity of 30 years to be developed in modules of equal capacity | [5 empty] | No Modules | 2
STP capacity for Stage 1 | [5 empty] | MLD | 39.9562

## SPS_Pumping Main
Table 3: Sewage Pumping Station
Sr. no | Design of Sewage Lifting Station | Unit | PS -1 | PS -2 | PS -3
A | Input Information: In yellow cells information to be filled as per particular requirement
1 | Peak Sewage flow | lps | 43.7 | 81.69 | 1173.11
2 | Peak factor |  | 3 | 2.5 | 2.25
3 | Liquid depth in wet well assumed | m | 2.2 | 2.2 | 2.2
9 | Invert Level | m | 207.5 | 207.5 | 202.76
10 | Ground Level | m | 211 | 211 | 207
11 | Delivery length of pumping Main | m | 150 | 150 | 600
12 | Level of Delivery Point above GL of SPS | m | 7 | 7 | 7.5
B | Review/Update If needed: In green cells review information and update if needed
4 | Detention time in Wetwell | mins | 20 | 20 | 20
5 | Velocity of flow during peak flow | m/s | 1.2 | 1.2 | 1.2
6 | Velocity of flow during average flow | m/s | 0.8 | 0.8 | 0.8
7 | Proposed pumps Working | numbers | 2 | 2 | 2
8 | Stand by pumps |  | 100% | 100% | 100%
13 | Material of pumping Main pipe |  | DI | DI | DI
C | Design of Sewage Pumping Station
1 | Peak Sewage flow | lpd | 3775680 | 7058016 | 101356704
2 | Average Sewage flow | lpd | 1258560 | 2823206.4 | 45047424
3 | Average Sewage flow | lps | 14.5667 | 32.676 | 521.3822
Wetwell Design
5 | Volume of the Wetwell Required | Cum | 17.48 | 39.2112 | 625.6587
7 | Area of the Wetwell Required | Sq.m | 7.9455 | 17.8233 | 284.3903
8 | Diameter of the wetwell | m | 3.1806 | 4.7637 | 19.0288
9 | Diameter of the wetwell, say | m | 3.5 | 5 | 19.5
10 | Diameter of pumping main for average flow | mm | 152.2615 | 228.0471 | 910.9366
11 | Diameter of pumping main for peak flow | mm | 215.3303 | 294.4075 | 1115.665
12 | Average dia for peak & average flow | mm | 183.7959 | 261.2273 | 1013.3008
13 | Dia of pumping main | m | 0.2 | 0.3 | 1.1
14 | Area of pumping main pipe | Sq. m | 0.031416 | 0.070686 | 0.95033
15 | Velocity in pipe for peak flow | m/s | 1.391 | 1.1557 | 1.2344
16 | Discharge in each Pump | lps | 21.85 | 40.845 | 586.555
17 | Discharge in each Pump | cum/hr | 78.7 | 147.1 | 2111.6
18 | Discharge in each Pump, say | cum/hr | 80 | 150 | 2120
19 | Pumping Head | m | 11.5 | 11 | 12.5
Hydraulic Details
20 | Depth | m | 3.5 | 3.5 | 4.24
21 | Head loss | m | 0.59899 | 0.42144 | 0.43459
22 | Total head required | m | 11.099 | 10.9214 | 12.1746
23 | KW required |  | 5 | 9 | 144
| KW required |  | 6 | 11 | 173
24 | Diameter of the pipe proposed | mm | 200 | 270 | 1100
D | Output Table
1 | Diameter of the wetwell | m | 3.5 | 5 | 19.5
2 | Discharge in each Pump | cum/hr | 80 | 150 | 2120
3 | Pumping Head | m | 11.5 | 11 | 173
4 | HP required of each pump |  | 6 | 11 | 144
5 | No of Pumps |  | 4 | 4 | 4
6 | Total KW |  | 24 | 44 | 576
7 | Diameter of the pipe proposed | mm | 200 | 270 | 1100
8 | Pipe Material |  | DI K7 | DI K7 | DI K7

## Estimate
Table 7: Estimate
S No | Item | Quantity | Rate | Units | Amount
Rs
1 | Sewer Net work | 205 | 5500000 | No | 1127500000
2 | Construction of Sewage Pump House | 644 | 25000 | KW | 16100000
3 | Construction of Sewage Treatment Plant | 39.9562 | 7000000 | MLD | 279693694.7689
4 | Cost of Land for STP, SPS | 15.9825 | 10000000 | Ha | 159824968.4394
5 | Sub Total |  |  |  | 1583118663.2083
6 | Physical Contingency | 10% |  |  | 158311866.3208
7 | Other contingencies | 5% |  |  | 79155933.1604
8 | Grand Total |  |  |  | 1820586462.6895